## BMS
| Basic Description | Brief Description | Pic | Model Code
1 | Differential Pressure Transmitter ( range : -100- 2500Pa) Without Display | DIFFERENTIAL PRESSURE TRANSMITTER Make: HK Instruments Oy (Made in Finland) Model: DPT2500-R8 Range: ±100, 100, 250, 500, 1000, 1500, 2000, 2500 Pa Zero Point Calibration: by Manual pushbutton Accuracy (from applied pressure): 1% Protection standard: IP54 Power supply: 24 VAC or VDC, ±10 % Output: 4 to 20 mA or 0 to 10 V, 3-wire Without Display |  | DPT2500-R8
2 | Differential Pressure Transmitter ( range : -100- 2500Pa) With Display | DIFFERENTIAL PRESSURE TRANSMITTER (With Display) Make: HK Instruments Oy (Made in Finland) Model: DPT2500-R8-D Range: ±100, 100, 250, 500, 1000, 1500, 2000, 2500 Pa Measuring units: Pa, kPa, mbar, inchWC, mmWC, psi, selectable via jumper Zero Point Calibration: by Manual pushbutton Accuracy (from applied pressure): 1% Protection standard: IP54 Power supply: 24 VAC or VDC, ±10 % Output: 4 to 20 mA or 0 to 10 V, 3-wire With Display |  | DPT2500-R8-D
3 | Differential Pressure Transmitter | Differential Pressure Transmitter, Model : DPT-Mini-1250 Make : HK Instruments Power Supply : 10...30 Vdc Voltage output : 0.5...4.5 V Pressure Range : 0...1250 Pa Accuracy : ±2 % FS (at 25 °C), max. ±3 % FS Ambient temperature : -10. 50 °C Ambient humidity : 0. 95 %rH Measurement units : Pa Protection class : IP54 Materials : ABS Cable : Type : fixed 3-wire cable Length: approx. 1 m, stripping length approx. 45 mm Wire : 0.25 mm2 (24 AWG), wire ends stripped and tinned, stripping length 8 mm Materials : PVC, copper, lead-free tin Dimensions (w x h x d) : 85 x 50 x 22 mm |  | DPT-Mini-1250
4 | AIR DIFFERENTIAL PRESSURE SWITCH | DIFFERENTIAL PRESSURE SWITCH Make : HK Instruments Oy Model : PS500 Range: 30-500 Pa, Supply voltage: 24–250 VAC, Output: NO / NC circuit, Protection class: IP54 |  | PS500
5 | AIR VELOCITY TRANSMITTER without Display | AIR VELOCITY TRANSMITTER Model : AVT Make : HK Instruments Oy Velocity ranges: 0...2 / 0...10 / 0...20 m/s Temperature range: 0...50 °C Probe: OD 10 mm, length 210 mm from bottom of the cover Immersion Length with Flange: Adjustable 50–180mm Supply voltage: 24 VDC/VAC ± 10% Output: 4-20 mA or 0-10 V Without Display |  | AVT
6 | AIR VELOCITY TRANSMITTER With Display | AIR VELOCITY TRANSMITTER Model : AVT-D Make : HK Instruments Oy Velocity ranges: 0...2 / 0...10 / 0...20 m/s Temperature range: 0...50 °C Probe: OD 10 mm, length 210 mm from bottom of the cover Immersion Length with Flange: Adjustable 50–180mm Supply voltage: 24 VDC/VAC ± 10% Output: 4-20 mA or 0-10 V With Display |  | AVT-D
7 | Air flow Transmitter | AIR FLOW & VELOCITY TRANSMITTER Make: HK Instruments Oy (Made in Finland) Model: DPT-Flow-1000-D Range: 0 ... 1000 Pa Multiple field selectable measurement units: o Volume flow: m3/s, m3/h, cfm, l/s o Velocity: m/s, ft./min o Pressure: Pa, inWC, mmWC, kPa, mbar, psi Zero Point Calibration: by pushbutton Supply Voltage: 24 VAC or VDC, ±10 % Output: 4 ... 20 mA or 0 ... 10 V, 3-wire Accuracy (from applied pressure): 1% Protection standard: IP54 Display: 2-line LCD display (12 characters/line) Line 1: Volume or velocity measurement Line 2: Pressure measurement |  | DPT-Flow-1000-D
8 | Air flow & Velocity Transmitter (DPT Range : 0-1000Pa) | AIR FLOW & VELOCITY TRANSMITTER Make: HK Instruments Oy (Made in Finland) Model: DPT-Flow-1000-AZ-D Range: 0 ... 1000 Pa Multiple field selectable measurement units: o Volume flow: m3/s, m3/h, cfm, l/s o Velocity: m/s, ft./min o Pressure: Pa, inWC, mmWC, kPa, mbar, psi Zero Point Calibration: by Automatic auto zero and by pushbutton Supply Voltage: 24 VAC or VDC, ±10 % Output: 4 ... 20 mA or 0 ... 10 V, 3-wire Accuracy (from applied pressure): 1% Protection standard: IP54 Display: 2-line LCD display (12 characters/line) Line 1: Volume or velocity measurement Line 2: Pressure measurement |  | DPT-Flow-1000-AZ- D
9 | Multipoint Averaging Pitot Tube Rectangular Duct | Averaging Flow Measuring Sensor for rectangular duct 1. Model: FloXact-L-150 / Length: 150 mm 2. 2. Model: FloXact-L-200 / Length: 200 mm 3. 3. Model: FloXact-L-250 / Length: 250 mm 4. 4. Model: FloXact-L-300 / Length: 300 mm 5. 5. Model: FloXact-L-350 / Length: 350 mm 6. 6. Model: FloXact-L-400 / Length: 400 mm 7. 7. Model: FloXact-L-450/ Length : 450 mm (select any one model ) Likewise we can provide upto 1500mm length
10 | Multipoint Averaging Pitot Tube Circular Duct | Averaging Flow Measuring Sensor for circular duct 1. Model: FloXact-R-150 / Length: 150 mm 2. 2. Model: FloXact-R-200 / Length: 200 mm 3. 3. Model: FloXact-R-250 / Length: 250 mm 4. 4. Model: FloXact-R-300 / Length: 300 mm 5. 5. Model: FloXact-R-350 / Length: 350 mm 6. 6. Model: FloXact-R-400 / Length: 400 mm 7. 7. Model: FloXact-R-450/ Length : 450 mm 8. (select any one model ) Likewise we can provide upto 1500mm length
11 | Electronic differential pressure switch(es) and transmitter, With Display | Differential Pressure Transmitter Make: DPI-24-2500-2R-D Model: Produal Oy Power Supply: 21...35 Vdc / 24 Vac ±10 % Output Signal: 4...20mA or 0...10 V 3 Wire Pressure Range: -100...+100 / 0...100 / 0...250 / 0...500 /0...1000 / 0...1500 /0...2000 / 0...2500 Pa Measurement units: Pressure: Pa, kPa, mbar, inchWC, mmWC Flow: m3/s, m3/hr, cfm, l/s, m/s, ft/min Relay outputs: (2 nos. Relay) 2 Relay : 30 Vdc, 6 A, spring-loaded terminal block (NC, COM, NO) Accuracy: ±1 % + ±2 Pa from reading Process connection: Ø5.2 mm horse, Brass Protection Class: IP54, With Display |  | DPI-24-2500-2R-D
12 | Differential Pressure or Air flow transmitter With PID Controller | DIFFERENTIAL PRESSURE OR AIR FLOW TRANSMITTER WITH PID CONTROLLER Make : HK Instruments Oy Model : DPT-Ctrl-2500-D Range: 0...2500 Pa Power supply: 24 VAC or VDC Output: • Control output: Voltage (0–10 V) or current (4–20 mA) • Differential pressure or air flow: Voltage (0–10 V) or current (4–20 mA) PID - Parameter: Adjustable Via Menu Zero Point Calibration: By Pushbutton with Display: 2-line display (12characters/line) Line 1: Direction of control output Line 2: Pressure or air flow measurement, (selectable via menu) IP Protection: IP54 |  | DPT-Ctrl-2500-D
HUMIDITY SENSOR
13 | Duct Mounted HUMIDITY & TEMPERATURE TRANSMITTER | HUMIDITY & TEMPERATURE TRANSMITTER Make : Produal Oy Model : KLK100 Measurement Range : Temperature: -50 ... 50 DegC Relative Humidity : 0- 100%rH Accuracy: Temperature: ±0.5 degree C Relative humidity: ±2 % Output: 0 ... 10 V or 4-20 mA Probe Dimension:∅ 8 mm x 220 mm Protection class:IP54 Without display Acc: with Adjustable flange |  | KLK100
14 | Outdoor/ Ambient Temp & Humidity transmitter | OUTDOOR HUMIDITY & TEMPERATURE TRANSMITTER Make : Produal Oy Model : KLU 100 Supply: 24 Vac/dc (22...28 V), 2 VA Range : Temperature: -50...50 °C Relative humidity: 0...100 %rH Output: 0...10 Vdc or4...20 mA Ambient temp: -50...50 °C Housing IP54 Mounting by screws Without display |  | KLU 100
15 | Room Humidity Transmitter & 0-10 V , without display | Room Humidity Transmitter Model : RTX-rH Make : Produal Oy Measurement Range: Temperature: 0....50°C Relative Humidity: 0- 100%rH Humidity Accuracy : 2% rH Temperature Accuracy : ±0.3 °C Operating temperature Range: 0 ... +50 °C Power supply: 24 VAC or VDC, ±10 %, Output: 0-10 V , Protection class: IP30 Without Display |  | RTX-rH
16 | Room Humidity Transmitter Without Display | Room Humidity & Temp. Transmitter Make : Produal Oy Model : KLH 100 Power supply : 24Vac/dc Humidity measurement range : 0...100%rH, Humidity accuracy : ±2 %rH Temperature measurement range :0...50 °C Temperature accuracy : ±0.5 °C, Humidity output : 0...10 Vdc, 2 mA Temperature output: 0...10 Vdc, 2 mA IP, protection class : IP20 Ambient temperature : 0...50 °C, Product dimensions : 87 x 86 x 30 mm Mounting on the wall surface or on a flush mounting box (60 mm hole distance), Materials : ABS plastic Without Display |  | KLH 100
17 | Room Humidity Transmitter With Display | Room Humidity & Temp. Transmitter Make : Produal Oy Model : KLH 100- N Power supply : 24Vac/dc Humidity measurement range : 0...100%rH, Humidity accuracy : ±2 %rH Temperature measurement range :0...50 °C Temperature accuracy : ±0.5 °C, Humidity output : 0...10 Vdc, 2 mA Temperature output: 0...10 Vdc, 2 mA IP, protection class : IP20 Ambient temperature : 0...50 °C, Product dimensions : 87 x 86 x 30 mm Mounting on the wall surface or on a flush mounting box (60 mm hole distance), Materials : ABS plastic With Display |  | KLH 100-N
CO2 SENSORS
| Room CO2 Transmitter | Room CO2 Transmitter Model : RT-CO2 Make: Produal Oy , Measurement Range: CO2: 0-2000 ppm, Temperature: 0....50°C, Operating temperature Range: 0 ...+50 °C, Power supply: 24 VAC or VDC, ±10 % Output: 0-10 V, Accuracy : 5 % of reading, Protection class: IP30, Materials : ABS plastic Without Display |  | RT-CO2
18 | Wall Co2 & Temperature Sensor With 0-10 V | Room CO2 Transmitter Make : Produal Oy Model : RTX-Co2 CO₂ measurement range : 0...5000 ppm CO₂ accuracy : With ABC calibration typ. ±40 ppm +2 % from reading, max. ±50 ppm +2 % from reading Temperature measurement range : 0...50 °C Temperature accuracy : ±0.3 °C Multifunctional output : 0...10 Vdc, 2 mA Multifunctional input : 1 x NTC 10 / Pt1000 / Resistive / Digital / 0...10 Vdc IP protection class : IP30 Product dimensions : 97 x 97 x 27 mm Materials : ABS plastic |  | RTX-Co2
| Room CO2 Transmitter | Room CO2 Transmitter, Model : RT-CO2-rH Make: Produal Oy , Co2 Measurement Range: CO2: 0-2000 ppm, Humidity measurement range : 0...100 %rH Temperature measurement range: 0....50°C, CO₂ accuracy : ±50 ppm +5 % Humidity accuracy : ±2 %rH Temperature accuracy : ±0.5 °C Operating temperature Range: 0 ...+50 °C, Power supply: 24 VAC or VDC, ±10 % Output: 0-10 V, Accuracy : 5 % of reading, Protection class: IP30, Materials : ABS plastic Without Display |  | RT-CO2-rH
19 | Wall Co2, Humidity temperature sensor with 0-10 V | Humidity & Temp. Transmitter, Make : Produal Oy Model : RTX-Co2-rH Measurement Range: Temperature: 0....50°C Relative Humidity: 0- 100%rH Operating temperature Range: 0 ... +50 °C CO₂ measurement range : 0...5000 ppm Power supply: 24 VAC or VDC, ±10 %, Output: 0-10 V , Accuracy : 2% rH Temperature Accuracy : ±0.3 °C, Protection class: IP30 Product dimensions : 97 x 97 x 27 mm Materials : ABS plastic Without Display |  | RTX-Co2-rH
20 | Outdoor CO2 Sensor | Outdoor CO2 Sensor Model : HDU Make: Produal Oy Co2 range: 0...2000 ppm Temperature measurement Range: -50...50 °C Accuracy (25 °C) : typ. ±40 ppm +3 % from reading (ABCLogicTM) Accuracy (25 °C) : ±0.5 °C Supply : 24 Vac/dc (22...28 V) < 10 VA Outputs : 0...10 V < 2 mA Operating conditions Operating conditions: Temperature-30...50 °C Humidity 0...85 % RH (non cond.) Housing IP54 Dimensions (w x h x d) 105 x 110 x 46 mm |  | HDU
| Duct Co2 Transmitter | Duct Co2 Transmitter, Model : HDK Make: Produal, Measurement Range: CO2: 0-2000 ppm Temperature: 0....50°C, Temperature accuracy : ±0.5 °C CO, accuracy : ±40 ppm +3 %, Operating temperature Range: 0 ... +50°C Calibration: Automatic self-calibration, ABC Logic TM, Power supply: 24 VAC or VDC, ±10 % Output: 0...10 V , Protection class: IP54 Product dimensions : 105 x 104 x 155mm, Without Display |  | HDK
21 | CO Sensor | CO Sensor Make : PRODUAL Oy Model : HML Supply 24 Vac/dc (22…28 V), 2 VA Range 0…100 ppm or 0…300 ppm* Accuracy (at 25 °C) : 10 ppm Output 0…10 Vdc or 4…20 mA Time constant : 1.5 min Operating temp. -30…40 °C Housing IP54, cable gland downwards Wall Mounting |  | HML
Indoor Air Quality
| Room Air Quality Transmitter | Room Air Quality Transmitter Model : RTX-D-RH Make : Produal Oy, Temperature Measurement Range: : 0....50°C Humidity measurement range : 0...100 % rH Humidity accuracy : ±2 % rH Temperature Accuracy : ±0.5 °C Power supply: 24 VAC or VDC, ±10 % Output: 0-10 V Protection class: IP30 Product dimensions : 97 x 97 x 27 mm Materials : ABS plastic With Display |  | RTX-D-RH
22 | Room CO2 Transmitter | Room CO2 Transmitter Make : Produal Oy Model : RTX-CO2-RH-VOC VOC measurement range : 0...65000 ppb (CO₂ equivalent: 400...2000 ppm) CO₂ measurement range : 0...5000 ppm Temperature Measurement Range: : 0....50°C Humidity measurement range : 0...100 % rH Humidity accuracy : ±2 % rH Temperature Accuracy : ±0.5 °C, Power supply: 24 VAC or VDC, ±10 %, Output: 0-10 V , Protection class: IP30 Product dimensions : 97 x 97 x 27 mm Materials : ABS plastic Without Display |  | RTX-CO2-RH-VOC
23 | Touchscreen Room Air Quality Transmitter | Touchscreen Room Air Quality Transmitter Model : RTX-CO2-D-RH-VOC Make : Produal Oy, VOC measurement range : 0...65000 ppb (CO2 equivalent: 400...2000 ppm) CO2 measurement range : 0...5000 ppm Temperature Measurement Range: : 0....50°C Humidity measurement range : 0...100 % rH Humidity accuracy : ±2 % rH Temperature Accuracy : ±0.5 °C Power supply: 24 VAC or VDC, ±10 % Output: 0-10 V Protection class: IP30 Product dimensions : 97 x 97 x 27 mm Materials : ABS plastic With Display |  | RTX-CO2-D-RH-VOC
24 | Room Air Quality Transmitter | Room Air Quality Transmitter Model : RTX-D-RH Make : Produal Oy, Temperature Measurement Range: : 0....50°C Humidity measurement range : 0...100 % rH Humidity accuracy : ±2 % rH Temperature Accuracy : ±0.5 °C Power supply: 24 VAC or VDC, ±10 % Output: 0-10 V Protection class: IP30 Product dimensions : 97 x 97 x 27 mm Materials : ABS plastic With Display |  | RTX-D-RH
| Room CO2 Transmitter | Room CO2 Transmitter, Model : RT-CO2-rH Make: Produal Oy , Co2 Measurement Range: CO2: 0-2000 ppm, Humidity measurement range : 0...100 %rH Temperature measurement range: 0....50°C, CO₂ accuracy : ±50 ppm +5 % Humidity accuracy : ±2 %rH Temperature accuracy : ±0.5 °C Operating temperature Range: 0 ...+50 °C, Power supply: 24 VAC or VDC, ±10 % Output: 0-10 V, Accuracy : 5 % of reading, Protection class: IP30, Materials : ABS plastic Without Display |  | RT-CO2-rH
| Wall Co2, Humidity temperature sensor with 0-10 V | Humidity & Temp. Transmitter, Make : Produal Oy Model : RTX-Co2-rH Measurement Range: Temperature: 0....50°C Relative Humidity: 0- 100%rH Operating temperature Range: 0 ... +50 °C CO₂ measurement range : 0...5000 ppm Power supply: 24 VAC or VDC, ±10 %, Output: 0-10 V , Accuracy : 2% rH Temperature Accuracy : ±0.3 °C, Protection class: IP30 Product dimensions : 97 x 97 x 27 mm Materials : ABS plastic Without Display |  | RTX-Co2-rH
25 | DUCT AIR QUALITY TRANSMITTER-VOC & TEMPERATURE | DUCT AIR QUALITY TRANSMITTER-VOC & TEMPERATURE Model : ILK-rH Make: HK Instruments Oy VOC measurement Rang : 450...2000 ppm (CO2 equivalent) Temperature measurement Range : 0...50 °C Humidity Measurement Range : 0...100 % RH warm up time 15 min output 0...10 V accuracy (25 °C) ±0.5 °C Operating conditions temperature: 0...+50°C humidity 0...85 % RH (non cond.) Housing IP54 Dimensions (w x h x d) 105 x 104 x 155mm |  | ILK-rH
Temperature sensor
26 | Room Temperature Sensor | Room Temperature Sensor Make : Produal Oy Model : RS PT-1000 Temperature measurement range : -30...70 °C Temperature measurement accuracy : ±0.3 °C Sensor : PT1000 RTD class IP protection class : IP30 Ambient temperature : -30...70 °C Ambient humidity : 0...95 % rH Product dimensions : 97 x 97 x 26 mm Materials : PC plastic |  | RS PT-1000
27 | Room Temperature Transmitter | Room Temperature Transmitter Model : RTX Make : Produal Oy Measurement Range: Temperature: 0....50°C Power supply: 24 VAC or VDC, ±10 %, Output: 0-10 V , Ambient humidity : 0...95 %rH Temperature Accuracy : ±0.3 °C, Protection class: IP30 Product dimensions : 97 x 97 x 27 mm Without Display |  | RTX
28 | Passive Immersion Sensor-resistive Output -You can select any of the below element: NTC 10; NTC 20; PT 1000; NI 1000; NI 1000-LG; NTC 1.8 | IMMERSION TEMPERATURE Sensor Make : Produal Oy Model : TEAT PT1000-150 Supply Voltage: 24vdc ....(15...35 Vdc) sensor: Pt1000 EN 60751/B Output : Resistive Range: -50........120 Dec Ambient temperature: 0...+60 °C Measuring probe dimensions :Ø 6 mm x 150 mm material : AISI 316L (acid-proof steel) IP protection :IP54 Ambient temperature : 0...60 °C Without Display With Thermowell |  | TEAT PT1000-150
29 | Immersion Temperature Transmitter -(4-20mA) | IMMERSION TEMPERATURE TRANSMITTE Make : Produal Oy Model : TEAT LL-150 Supply Voltage: 24vdc ....(15...35 Vdc) sensor: Pt1000 EN 60751/B Output: 4-20mA, 2Wire Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Ambient temperature: 0...+60 °C Measuring probe dimensions :Ø 6 mm x 80 mm material : AISI 316L (acid-proof steel) IP protection :IP54 Ambient temperature : 0...60 °C Probe length : 150 mm, With Thermowell |  | TEAT LL -150
30 | Immersion temperature transmitter -(0-10V ) | IMMERSION TEMPERATURE TRANSMITTE -(0-10V ) Model : TEAT LU-150 Make : Produal Oy Supply Voltage: 24vdc ....(15...35 Vdc) sensor: Pt1000 EN 60751/B Output : 0-10 V Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Ambient temperature: 0...+60 °C Measuring probe dimensions :Ø 6 mm x 150 mm material : AISI 316L (acid-proof steel) IP protection :IP54 Ambient temperature : 0...60 °C Without Display |  | TEAT LU-150
31 | Passive Air duct temperature sensor - resistive Output ; You can select any of the below element :- NTC 10; NTC 20: PT 1000 ; NI 1000; NI 1000-LG;NTC 1.8 | TEMPERATURE SENSOR (Duct Mounted) Model :TEK PT1000 Make: Produal Oy Duct mounted sensor sensor: Pt1000 EN 60751/B output: Resistive Range: -50....70 °C Accuracy: ±0.3 °C (0 °C) Mounting: Duct adjustable via flange stem :Ø 8 mm x 200 mm, materialAISI316 housing: plastics protection class: IP54 ambient temperature: 0...+60 °C Transmitter type: 2-wire Without display |  | TEK PT1000
32 | Duct Temperature Sensor(0..10VDC output) | TEMPERATURE TRANSMITTER Make: Produal Oy Model :TEK LU Duct mounted sensor sensor: Pt1000 EN 60751/B output: 0...10 V Range: -50...50, -50...150, 0...50, 0...100 °C (selectablevia jumper) Mounting: Ductadjustablevia flange stem :Ø 8 mm x 200 mm, materialAISI316 housing: plastics protection class: IP54 ambient temperature: 0...+60 °C Transmitter type: 2-wire Without display |  | TEK LU
33 | Duct Temperature Sensor(4…20mA output) | TEMPERATURE TRANSMITTER Make: Produal Oy Model :TEK LL Duct mounted sensor sensor: Pt1000 EN 60751/B output: 4-20 mA Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Mounting: Duct adjustable via flange stem :Ø 8 mm x 200 mm, materialAISI316 housing: plastics protection class: IP54 ambient temperature: 0...+60 °C Transmitter type: 2-wire Without display |  | TEK LL
34 | CABLE TEMPERATURE TRANSMITTER | CABLE TEMPERATURE TRANSMITTER Model : TEKY4LL Make : Produal Oy Ranges 0...50 °C 0...100 °C -50...50 °C -50... 150 °C Supply : 15...35 Vdc Sensor element: Pt1000 EN60751/B Accuracy ±0.5 °C Output : 4...20mA 2-wire, temperature transmitter for cold spaces Measuring probe sleeve : 4 mm x 30 mm, stainless steel ambient temperature -30...+80 °C cable : 3.2 mm x 2.3 m cable gland : M16 ambient temperature : -30...60 °C protection class IP54 Without Display |  | TEKY4 LL
35 | CABLE TEMPERATURE TRANSMITTER | CABLE TEMPERATURE SENSOR Make : Produal Oy Model : TEKY4 PT 1000 Temperature measurement range: -30...80 °C Supply : 15...35 Vdc Sensor element: Pt1000 EN60751/B Temperature measurement accuracy : ±0.3 °C (0 °C) Output : resistive Measuring probe sleeve : 4 mm x 30 mm, stainless steel ambient temperature -30...+80 °C cable : 3.2 mm x 2.3 m cable gland : M16 ambient temperature : -30...60 °C protection class IP54 |  | TEKY4 PT 1000
36 | Cable Temperature Sensors NTC PROBE | Cable Temperature Sensors NTC PROBE Make : Pixsys Model : TYPE 1 SERIES: NTC PROBE CO-PRINTED WITH IP 67 PLATE (2-WIRE) SENSORS : NTC 10K 1% BETA 3435 1% [ 5SENSMD001 ] SMD CAPSULE : Ø5 mm - 6 mm X 15 mm. THERMOPLASTIC RUBBER CABLE TYPE: THERMOPLASTIC RUBBER PLATE [ 9CAVPIAT003 ] LUNGH. 6 METERS CABLE COLOUR: CABLE ( BLACK ) CORES ( BLACK ) CABLE CROSS-SECTION: CROSS-SECTION 2X0.25 MM2 1.65 MM X 3.60 MM CABLE/CAPSULE CONNECTION : NONE CONNECTORS/TERMINALS : TINNED FILLER : THERMOPLASTIC RUBBER WORKING RANGE: ( -50+120 )°C DEGREE OF PROTECTION: IP 67 |  | TYPE 1
37 | Cable Temperature Sensors NTC PROBE WITH BRACELET | Cable Temperature Sensors NTC PROBE WITH BRACELET Make : Pixsys Model : TYPE 2 SERIES : NTC PROBE WITH BRACELET WITH DIAMETER FROM Ø4 TO 30 MM TUBES ( 2WIRES ) SENSORS : NTC 10K 1% BETA 3435 1% [ 5SENSMD001 ] SMD CAPSULE : Ø6 mm X 20 mm. THERMOPLASTIC RUBBER CABLE TYPE: THERMOPLASTIC RUBBER PLATE LUNGH. 6 METERS CABLE COLOUR: CABLE ( BLACK ) CORES ( BLACK ) CABLE CROSS-SECTION: CROSS-SECTION 2X0.25 MM2 1.65 MM X 3.60 MM CABLE/CAPSULE CONNECTION : NONE CONNECTORS/TERMINALS : TINNED FILLER : THERMOPLASTIC RUBBER WORKING RANGE: ( -50+120 )°C DEGREE OF PROTECTION: IP 67 |  | TYPE 2
38 | Room Temperature Transmitter -(4-20mA) | ROOM TEMPERATURE TRANSMITTER -(4-20mA) Model : TEHR LL Make : Produal Oy measuring ranges selectable : 0...+50 °C 0...+100 °C -50...+50 °C -50...+150 °C supply : 15...35 Vdc output : 4...20 mA accuracy : ±0.5 °C at 25 °C ambient temperature : 0...+50 °C housing ABS plastic: IP20 dimensions : (w x h x d) 86 x 85 x 32 mm |  | TEHR LL
39 | Outdoor/ Ambient Temperature Transmitter ( 4-20mA) | OUTDOOR/ AMBIENT TEMPERATURE TRANSMITTER Make : Produal Oy Model : TEU LL Sensor element : Pt1000 EN 60751/B Supply : 15...35 Vdc output: 4...20 mA, 2 wire Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Housing protection class IP54 (cable gland downwards) cable gland M16 dimensions (w x h x d) 115 x 115 x 45 mm Ambient temperature -30...60 °C |  | TEU LL
40 | Vibration Sensor | Vibration Sensor Make: Hauber Model: HE090-00-25-00-00-000 Frequency range: 10...1000 Hz, Output 1 : 4-20 mA (proportional to the measuring range) 2 wire Measuring Range 0...25 mm/s rms, Max. acceleration: ±16,5 g Ambient Temperature : -40...+60 °C Measuring Head Temperature : -40...+125 °C Supply voltage: 10...30 V DC Housing: V2A stainless steel 1.4305, Connection: M12 plug, Protection: IP 66/67 |  | HE090-00-25-00-00-000

## EMS
| Basic Description | Brief Description | Pic | Model Code
1 | DIFFERENTIAL PRESSURE TRANSMITTER | DIFFERENTIAL PRESSURE TRANSMITTER Make: HK Instruments Oy (Made in Finland) Model : DPT250-R8 Range: ±25, ±50, ±100, ±150 ,25, 50, 100, 250 Pa Zero Point Calibration: by Manual pushbutton Accuracy (from applied pressure): 1% Protection standard: IP54 Power supply: 24 VAC or VDC, ±10 % Output: 4 to 20 mA or 0 to 10 V, 3-wire Without Display |  | DPT250-R8
2 | Differential Pressure Transmitter with Display ( range : -150- 250Pa) | DIFFERENTIAL PRESSURE TRANSMITTER (With Display) Make: HK Instruments Oy (Made in Finland) Model : DPT250-R8-D Range: ±25, ±50, ±100, ±150 ,25, 50, 100, 250 Pa Pressure units (select via menu): Pa, kPa, mbar, inWC, mmWC, psi Zero Point Calibration: by Manual pushbutton Accuracy (from applied pressure): 1% Protection standard: IP54 Power supply: 24 VAC or VDC, ±10 % Output: 4 to 20 mA or 0 to 10 V, 3-wire With Display |  | DPT2500-R8-D
3 | Differential Pressure Transmitter without Display ( range : -150- 250Pa) With Autozero (-AZ) | DIFFERENTIAL PRESSURE TRANSMITTER (Without Display) Make: HK Instruments Oy (Made in Finland) Model : DPT250-R8-AZ Range: ±25, ±50, ±100, ±150 ,25, 50, 100, 250 Pa Zero Point Calibration: by Automatic auto zero (AZ) and by pushbutton Accuracy (from applied pressure): 1% Protection standard: IP54 Power supply: 24 VAC or VDC, ±10 % Output: 4 to 20 mA or 0 to 10 V, 3-wire Without Display |  | DPT250-R8-AZ
4 | Differential Pressure Transmitter with Display ( range : -150- 250Pa) With Autozero (-AZ) | DIFFERENTIAL PRESSURE TRANSMITTER (With Display) Make: HK Instruments Oy (Made in Finland) Model : DPT250-R8-AZ-D Range: ±25, ±50, ±100, ±150 ,25, 50, 100, 250 Pa Measuring units: Pa, kPa, mbar, inchWC, mmWC, psi, selectable via jumper Zero Point Calibration: by Automatic auto zero (AZ) and by pushbutton Accuracy (from applied pressure): 1% Protection standard: IP54 Power supply: 24 VAC or VDC, ±10 % Output: 4 to 20 mA or 0 to 10 V, 3-wire With Display |  | DPT250-R8-AZ-D
5 | Room Temperature Transmitter | Room Temperature Transmitter Model : RTX Make : Produal Oy Measurement Range: Temperature: 0....50°C Power supply: 24 VAC or VDC, ±10 %, Output: 0-10 V , Ambient humidity : 0...95 %rH Temperature Accuracy : ±0.3 °C, Protection class: IP30 Product dimensions : 97 x 97 x 27 mm Without Display |  | RTX
6 | Room Humidity Transmitter | Room Humidity Transmitter Model : RTX-rH Make : Produal Oy Measurement Range: Temperature: 0....50°C : Relative Humidity: 0- 100%rH Operating temperature Range: 0 ... +50 °C Power supply: 24 VAC or VDC, ±10 %, Output: 0-10 V , Accuracy : 2% rH Temperature Accuracy : ±0.3 °C, Protection class: IP30 Without Display |  | RTX-rH
7 | Room Humidity Transmitter | Room Humidity Transmitter Model : RTX-D-rH Make : Produal Oy Measurement Range: Temperature: 0....50°C Relative Humidity: 0- 100%rH Humidity Accuracy : 2% rH Temperature Accuracy : ±0.3 °C Operating temperature Range: 0 ... +50 °C Power supply: 24 VAC or VDC, ±10 %, Output: 0-10 V , Protection class: IP30 With Display |  | RTX-D-RH
8 | Duct Temp. & Humidity | HUMIDITY & TEMPERATURE TRANSMITTER Make : Produal Oy Model : KLK100 Measurement Range : Temperature: -50 ... 50 DegC Relative Humidity : 0- 100%rH Accuracy: Temperature: ±0.5 degree C Relative humidity: ±2 % Output: 0 ... 10 V or 4-20 mA Probe Dimension:∅ 8 mm x 220 mm Protection class:IP54 Without display Acc: with Adjustable flange |  | KLK100
9 | Duct Temperature Sensor(4…20mA output) | TEMPERATURE TRANSMITTER Make: Produal Oy Model :TEK LL Duct mounted sensor sensor: Pt1000 EN 60751/B output: 4-20 mA Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Mounting: Duct adjustable via flange stem :Ø 8 mm x 200 mm, materialAISI316 housing: plastics protection class: IP54 ambient temperature: 0...+60 °C Transmitter type: 2-wire Without display |  | TEK LL

## WATER- CHILLER
| Basic Description | Brief Description | Pic | Model Code
1 | Passive immersion sensor-resistive Output -You can select any of the below element: NTC 10; NTC 20; PT 1000; NI 1000; NI 1000-LG; NTC 1.8 | IMMERSION TEMPERATURE Sensor Make : Produal Oy Model : TEAT PT1000-150 Supply Voltage: 24vdc ....(15...35 Vdc) sensor: Pt1000 EN 60751/B Output : Resistive Range: -50........120 Dec Ambient temperature: 0...+60 °C Measuring probe dimensions :Ø 6 mm x 150 mm material : AISI 316L (acid-proof steel) IP protection :IP54 Ambient temperature : 0...60 °C Without Display With Thermowell |  | TEAT PT1000-150
2 | Immersion Temperature Transmitter -(4-20mA) | IMMERSION TEMPERATURE TRANSMITTE Make : Produal Oy Model : TEAT LL-150 Supply Voltage: 24vdc ....(15...35 Vdc) sensor: Pt1000 EN 60751/B Output: 4-20mA, 2Wire Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Ambient temperature: 0...+60 °C Measuring probe dimensions :Ø 6 mm x 80 mm material : AISI 316L (acid-proof steel) IP protection :IP54 Ambient temperature : 0...60 °C Probe length : 150 mm, With Thermowell |  | TEAT LL-150
3 | Immersion temperature transmitter -(0-10V ) | IMMERSION TEMPERATURE TRANSMITTE -(0-10V ) Model : TEAT LU-150 Make : Produal Oy Supply Voltage: 24vdc ....(15...35 Vdc) sensor: Pt1000 EN 60751/B Output : 0-10 V Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Ambient temperature: 0...+60 °C Measuring probe dimensions :Ø 6 mm x 150 mm material : AISI 316L (acid-proof steel) IP protection :IP54 Ambient temperature : 0...60 °C Without Display |  | TEAT LU-150
4 | Differential Pressure Transmitter for liquids (0-6, 2.5,10 bar Any range ) | Differential Pressure Transmitter for liquids Make: Beck GmbH (Made in Germany) Model: 988.213A1 Pressure range: 0 to 6 Bar Material of pressure chamber: Brass Output signal: 4-20mA, 2-wire Process connection: G ¼ Electrical connection: Connection plug EN 175301-803 Form A, including female power connector |  | 988.213A1
5 | Liquid Dp switch ( range can be select from datasheet ) | Differential Pressure Switch for liquids Make: Beck GmbH (Made in Germany) Model: 908.34111M421 Range: 0.15 to 1 bar Overpressure range: 10 bar Repeatability: ±10 % Temperature of media from -10 to +80°C Diaphragm: NBR Pressure connection: Inner thread G 1/8 of Brass (CuZn40) P1+ / P2– Switch type: 1 SPDT Contacts rating: 6A / 250VAC AgNi Electrical connection: Tab terminal 6.3 mm x 0.8 mm Protection: Protection cap IP65 with cable conduit M16 Mounting: L-shaped bracket |  | 908.34111M421
6 | Pressure Transmitter | Pressure Transmitter, Model: TFP-40S-0100-G-42-01-D-Ix-G4 (0 to 10bar) Make : Trumen, Pressure Range: 0....10 bar, Pressure Type: gauge, Output Signal: 4...20mA, Accuracy: 0.5% FSO, Electrical Connection: Connector DIN43650, Indicator: Without Indicator, Process Connection: G 1/4’’ Male, |  | TFP-40S-0100-G-42-01-D-Ix-G4
7 | Level switch | CABLE FLOAT LEVEL SWITCH Make : Trumen Technologies Model : LCF-R-SPDT 10A -5M Type R : Rectangular Output : SPDT 1 NO/1NC Rated Switching Capacity : 10V... 240Vac Protection Degree : IP68 Housing Cable Length : 5Meter |  | LCF-R-SPDT 10A -5M
8 | Level Transmitter (considering 5 Meter tank ) | HYDROSTATIC LEVEL TRANSMITTER Make : Trumen Technologies Model : TLH-HAN-F003-C4-DLP-B5-L5000mm Enclosure: Aluminum Non-Hazardous IP-67/68 Process Connection: Flange type:1" B16.5 ANSI/ASA 150#RF Process Connection Material: SS304 Output: DC Loop Powered 4-20mA Pressure Range in Meters:0...5mH2O Cable Length: 5Meter |  | TLH-HAN-F003-C4-DLP-B5-L5000mm
9 | Level switch DG tank ( Considering 1 meter tank ) | CAPACITANCE LEVEL SWITCH Make : Trumen Technologies Model : LMC-HAN-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm HAN: Enclosure Aluminum Non-Hazardous IP-67/68, T1:Material Temperature max 80*DegC, RD1: Sensor Type Single Rigid Rod probe, S4: Sensing Rope Material SS 304, IT: Insulation Type full PTFE insulated, G0: Inactive length None, W4: Stilling well material SS 304 PB2:Process Connection Type 1-1/2" BSP, C4:Process Connection Material SS 304, EIUSI: 2 SPDT relay O/P for 2 single point L1000mm: Probe Length 1meter length |  | LMC-HAN-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm
10 | Level switch DG tank Flameproof ( Considering 1 meter tank ) | CAPACITANCE LEVEL SWITCH Model : LMC-HAX-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm Make : Trumen Technologies HAX: Aluminum Flameproof IIa, IIb and IIc T1:Material Temperature max 80*DegC, RD1: Sensor Type Single Rigid Rod probe, S4: Sensing Rope Material SS 304, IT: Insulation Type full PTFE insulated, G0: Inactive length None, W4: Stilling well material SS 304 PB2:Process Connection Type 1-1/2" BSP, C4:Process Connection Material SS 304, EIUSI: 2 SPDT relay O/P for 2 single point L1000mm: Probe Length 1meter length |  | LMC-HAX-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm
11 | Level Transmitter DG tank ( Considering 1 meter tank ) | CAPACITANCE LEVEL TRANSMITTER Model : TLC-HAN-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm Make : Trumen Technologies HAN: Enclosure Aluminum Non-Hazardous IP-67/68, T1:Material Temperature max 80*DegC, RD1: Sensor Type Single Rigid Rod probe, S4: Sensing Rope Material SS 304, IT: Insulation Type full PTFE insulated, G0: Inactive length None, W4: Stilling well material SS 304 PB2:Process Connection Type 1-1/2" BSP, C4:Process Connection Material SS 304, EIL: 4-20mA Loop powered O/P L1000mm: Probe Length 1meter length |  | TLC-HAN-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm
12 | Level Transmitter DG tank ( Considering 1 meter tank ) | CAPACITANCE LEVEL TRANSMITTER Model : TLC-HAX-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm Make : Trumen Technologies HAX: Aluminum Flameproof IIa, IIb and IIc T1:Material Temperature max 80*DegC, RD1: Sensor Type Single Rigid Rod probe, S4: Sensing Rope Material SS 304, IT: Insulation Type full PTFE insulated, G0: Inactive length None, W4: Stilling well material SS 304 PB2:Process Connection Type 1-1/2" BSP, C4:Process Connection Material SS 304, EIL: 4-20mA Loop powered O/P L1000mm: Probe Length 1meter length |  | TLC-HAX-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm
13 | Ultrasonic Level Transmitter | Ultrasonic Level Transmitter, Model : TLU(N)-05-G2-I2-S1-E2 Make: Trumen, Make: Trumen, Performance : Normal usable in non-explosive areas only Measuring Range : 0...5 m Process connection: G2" male thread, Output signal : 4~20 mA-2wire, Power supply :24VDC Accuracy : 0.5%F.S |  | TLU(N)-05-G2-I2-S1-E2
14 | Water Level Transmitter | Water Level Transmitter Model : 981.08001L208 (0 ... +600 mbar) Make: Beck GmbH (Made in Germany) Pressure Range: 0-600 mbar (That indicates the level range up to 6 meter tank) Supply voltage: 10 .. 30 VDC Output: 2-wire; 4 - 20 mA Process connection: Brass thread, G1/4 Electrical connection: AMP connection M12; 4-pole Protection class: IP65 Temperature range: –20°C .. +85°C Linearity error: = ±1% Accessories: M12 connector with 5-meter cable |  | 981.08001L208
15 | Transmitter (dual Channel) | Transmitter (dual Channel) Model : 46 series Make : Chemitec Dual Channel Anlyzer Wall mounting : 144X144 Measuring range in reference with connected electrode/sensors. Graphic display 128 x 128. Internal data logger. Analogue output: 2 x 4...20 mA 800Ohm. Digital Output: 2 x Relays: 250 VAC 5 A; RS485 Serial port MODBUS RTU communication Power Supply: 100...230Vac |  | 46 series
16 | Free Chlorine | S494N/CL/5/mA SW Make : Chemitec Free Chlorine Sensor output: 4-20 mA range: 0- 02,5,10,20,200,2000 ppm |  | S494N/CL/5/mA
17 | PH ELECTRODE | PH ELECTRODE Make : Chemitec Model : S401 V/G pH Glass, combined pH Electrode S7 head 5m cable pH Electrode for general Application Glass, combined pH Electrode (Ø=12mm. L=120mm.) with integrated PG 13.5 thread Measuring range 0.00÷14.0 pH Max working temperature 80°C. Max working pressure 6 bar Min. conductivity 5µS. Threaded head S/7. 5 mt. cable, with threaded connection |  | S401 V/G
18 | ORP ELECTRODE | ORP ELECTRODE Model : S406 VG Make: Chemitec Materials: Glass shaft, Platinum wire, partly melted into glass membrane Thread :PG13,5 Range :-999 … +999mV Max working temperature: 80°C Max working pressure: 6 bar Electrolyte: polymeric electrolyte Sample: min Conductivity: 5 μS/cm Diaphragm :Single Pore Number of Diaphragm: 1 Connection type :S8 Temperature Sensor :No ATEX Approval: No Recommended storage: 3M KCl |  | S406 VG
19 | CONDUCTIVITY SENSOR & TRANSMITTER/TDS Meter | CONDUCTIVITY SENSOR & TRANSMITTER Model : S411 (THERMO COMPENSATED CONDUCTIVITY CELL) Make : Chemitec Materials • PSU Body • Graphite Electrodes • O-Ring BNC • Temperature sensor embedded in an INOX case, in direct contact with the liquid • Waterproof connector Thread :1/2” GAS or 1” GAS Cell’s constants K = 0.1 cm, K = 1 cm, K = 10 cm Cable length 5m (10m or 15m available on request) Max working temperature 120°C Operating pressure 6 Bar at 20°C / 2 Bar at 120°C Measuring range (K = 10 cm) 0-200 μS - (K = 1 cm) 0-50000 μS - (K = 0.1 cm) 10-200 mS |  | S411 (THERMO COMPENSATED CONDUCTIVITY CELL)
20 | Turbidity Transmitter | Turbidity Transmitter, Model : 50Series_COD: 9740610010A Make: Chemitec -2 Dig. plug play analyzer 2 par. Modbus Wall 220V 50 Series Multiparametric Controller Possibility of connecting up to 8 sensors. Color Graphic LCD 480 x 272 display. Five key for programming Internal data logger, Download data via USB Pen stick. Four a Analog outputs 4...20mA 500Ohm. Six Digital output for Set Point and alarm Serial port RS485 with MODBUS RTU protocol ( other on request ). Power supply 90 ÷ 240Vac 47 ÷ 63Hz ( 24Vac/dc on request) Wall mounting ABS box. Protection IP 66 Size 144x144x122 mm, 5 (D) Weight 1.0 Kg Turbidity Sensor, Model : S461LT PVC_COD: 9701072063 Make:Chemitec, Turbidity Probe with RS485 output 90° scattered light measuring principle ISO 7027 / EN 27027 Wavelength 880nm pulsed light method Measuring ranges: 0-10 NTU, 0-100NTU, Resolution 0,01/0,1NTU Accuracy: ± 1..5 %, Operating temperature: 0….40C° Max Operating Pressure: 4bar Material: PVC , Glass Dimensions (Ø x L): 42x231mm. Cable 10m cable and connector. Mechanical protection: IP68 Sensor + Cable Probe Holder Turbidity Sensor: Model :PSS 8-B1_COD: 9900103086 Make: Chemitec, PSS8 D42-D36-D33 By-pass cell with black vessel PSS 8-B1 Downflow probe holder for SX461/LT by-pass installation flow switch included, 2 bar max. , 40°C, black beaker Inlet - Outlet dimensions 8x12mm |  | 50Series_COD: 9740610010A + S461LT PVC_COD: 9701072063 + SS 8-B1_COD: 9900103086
21 | Immersion Tempereture Sensor | RTD Sensor, RRT-101-A-2-T2-A-3W-6-SL-12B-WPS-08 (300) Make: Parshvi, Process Connection : Welded Thread Element Type : 1 X PT 100 Simplex Temperature Range : -50C to 250C Accuracy : Class 'A' Wire Configuration : 3wire Sheath Diameter -D : 6.0 mm Sheath Length-SL : 300 mm Process Connection Size : 1/2" BSP (M) Enclosure Type : Screwed Type weatherproof Die Cast Aluminum Single Cable Entry IP-67 Other Options : Head mounted Temperature transmitter 2 Temp. Transmitter (RFID), Model : 2000.35.010 Make: Pixsys Input: RTD (PT100/NI100/PT1000), Output: 4...20mA Loop Powered |  | RTD Sensor & TT
22 | Vibration Sensor | Vibration Sensor Make: Hauber Model: HE090-00-25-00-00-000 Frequency range: 10...1000 Hz, Output 1 : 4-20 mA (proportional to the measuring range) 2 wire Measuring Range 0...25 mm/s rms, Max. acceleration: ±16,5 g Ambient Temperature : -40...+60 °C Measuring Head Temperature : -40...+125 °C Supply voltage: 10...30 V DC Housing: V2A stainless steel 1.4305, Connection: M12 plug, Protection: IP 66/67 |  | HE090-00-25-00-00-000

## FIRE
| Basic Description | Brief Description | Pic | Model Code
1 | Differential Pressure Transmitter without Display ( range : -100- 2500Pa) | DIFFERENTIAL PRESSURE TRANSMITTER Make: HK Instruments Oy (Made in Finland) Model: DPT2500-R8 Range: ±100, 100, 250, 500, 1000, 1500, 2000, 2500 Pa Zero Point Calibration: by Manual pushbutton Accuracy (from applied pressure): 1% Protection standard: IP54 Power supply: 24 VAC or VDC, ±10 % Output: 4 to 20 mA or 0 to 10 V, 3-wire Without Display |  | DPT2500-R8
2 | Differential Pressure Transmitter with Display ( range : -100- 2500Pa) | DIFFERENTIAL PRESSURE TRANSMITTER (With Display) Make: HK Instruments Oy (Made in Finland) Model: DPT2500-R8-D Range: ±100, 100, 250, 500, 1000, 1500, 2000, 2500 Pa Measuring units: Pa, kPa, mbar, inchWC, mmWC, psi, selectable via jumper Zero Point Calibration: by Manual pushbutton Accuracy (from applied pressure): 1% Protection standard: IP54 Power supply: 24 VAC or VDC, ±10 % Output: 4 to 20 mA or 0 to 10 V, 3-wire With Display |  | DPT2500-R8-D
3 | Differential Pressure Switch (30-500 Pa) | DIFFERENTIAL PRESSURE SWITCH Make : HK Instruments Oy Model : PS500 Range: 30-500 Pa, Supply voltage: 24–250 VAC, Output: NO / NC circuit, Protection class: IP54 |  | PS500
4 | Duct Mounted HUMIDITY & TEMPERATURE TRANSMITTER | HUMIDITY & TEMPERATURE TRANSMITTER Make : Produal Oy Model : KLK100 Measurement Range : Temperature: -50 ... 50 DegC Relative Humidity : 0- 100%rH Accuracy: Temperature: ±0.5 degree C Relative humidity: ±2 % Output: 0 ... 10 V or 4-20 mA Probe Dimension:∅ 8 mm x 220 mm Protection class:IP54 Without display Acc: with Adjustable flange |  | KLK100
5 | Passive immersion sensor-resistive Output -You can select any of the below element: NTC 10; NTC 20; PT 1000; NI 1000; NI 1000-LG; NTC 1.8 | IMMERSION TEMPERATURE Sensor Make : Produal Oy Model : TEAT PT1000-150 Supply Voltage: 24vdc ....(15...35 Vdc) sensor: Pt1000 EN 60751/B Output : Resistive Range: -50........120 Dec Ambient temperature: 0...+60 °C Measuring probe dimensions :Ø 6 mm x 150 mm material : AISI 316L (acid-proof steel) IP protection :IP54 Ambient temperature : 0...60 °C Without Display With Thermowell |  | TEAT PT1000-150
6 | Immersion Temperature Transmitter -(4-20mA) | IMMERSION TEMPERATURE TRANSMITTE Make : Produal Oy Model : TEAT LL-150 Supply Voltage: 24vdc ....(15...35 Vdc) sensor: Pt1000 EN 60751/B Output: 4-20mA, 2Wire Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Ambient temperature: 0...+60 °C Measuring probe dimensions :Ø 6 mm x 80 mm material : AISI 316L (acid-proof steel) IP protection :IP54 Ambient temperature : 0...60 °C Probe length : 150 mm, With Thermowell |  | TEAT LL -150
7 | Immersion temperature transmitter -(0-10V ) | IMMERSION TEMPERATURE TRANSMITTE -(0-10V ) Model : TEAT LU-150 Make : Produal Oy Supply Voltage: 24vdc ....(15...35 Vdc) sensor: Pt1000 EN 60751/B Output : 0-10 V Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Ambient temperature: 0...+60 °C Measuring probe dimensions :Ø 6 mm x 150 mm material : AISI 316L (acid-proof steel) IP protection :IP54 Ambient temperature : 0...60 °C Without Display |  | TEAT LU-150
8 | Water Level Transmitter | Water Level Transmitter Make: Beck GmbH (Made in Germany) Model: 981.08001L208 (0 ... +600 mbar) Pressure Range: 0-600 mbar Supply voltage: 10 .. 30 VDC Output: 2-wire; 4 - 20 mA Process connection: Brass thread, G1/4 Electrical connection: AMP connection M12; 4-pole Protection class: IP65 Temperature range: –20°C .. +85°C Linearity error: = ±1% Accessories: M12 connector with 5-meter cable |  | 981.08001L208
9 | Liquid Dp switch ( range can be select from datasheet ) | Differential Pressure Switch for liquids Make: Beck GmbH (Made in Germany) Model: 908.34111M421 Range: 0.15 to 1 bar Overpressure range: 10 bar Repeatability: ±10 % Temperature of media from -10 to +80°C Diaphragm: NBR Pressure connection: Inner thread G 1/8 of Brass (CuZn40) P1+ / P2– Switch type: 1 SPDT Contacts rating: 6A / 250VAC AgNi Electrical connection: Tab terminal 6.3 mm x 0.8 mm Protection: Protection cap IP65 with cable conduit M16 Mounting: L-shaped bracket |  | 908.34111M421
10 | Differential Pressure Transmitter for liquids (0-6, 2.5,10 bar Any range ) | Differential Pressure Transmitter for liquids Make: Beck GmbH (Made in Germany) Model: 988.213A1 Pressure range: 0 to 6 Bar Material of pressure chamber: Brass Output signal: 4-20mA, 2-wire Process connection: G ¼ Electrical connection: Connection plug EN 175301-803 Form A, including female power connector |  | 988.213A1
11 | Pressure Transmitter | Pressure Transmitter, Model: TFP-40S-0100-G-42-01-D-Ix-G4 (0 to 10bar) Make : Trumen, Pressure Range: 0....10 bar, Pressure Type: gauge, Output Signal: 4...20mA, Accuracy: 0.5% FSO, Electrical Connection: Connector DIN43650, Indicator: Without Indicator, Process Connection: G 1/4’’ Male, |  | TFP-40S-0100-G-42-01-D-Ix-G4 (0 to 10bar)
12 | Level switch | CABLE FLOAT LEVEL SWITCH Make : Trumen Technologies Model : LCF-R-SPDT 10A -5M Type R : Rectangular Output : SPDT 1 NO/1NC Rated Switching Capacity : 10V... 240Vac Protection Degree : IP68 Housing Cable Length : 5Meter |  | LCF-R-SPDT 10A -5M
13 | Level Transmitter (considering 5 Meter tank ) | HYDROSTATIC LEVEL TRANSMITTER Make : Trumen Technologies Model : TLH-HAN-F003-C4-DLP-B5-L5000mm Enclosure: Aluminum Non-Hazardous IP-67/68 Process Connection: Flange type:1" B16.5 ANSI/ASA 150#RF Process Connection Material: SS304 Output: DC Loop Powered 4-20mA Pressure Range in Meters:0...5mH2O Cable Length: 5Meter |  | TLH-HAN-F003-C4-DLP-B5-L5000mm
14 | Duct Smoke Detector | Duct Smoke Detector - Model : KRM-X-2-0,16 Make: Oppermann Regelgeräte GmbH Duct type prob length: 160 mm Sensor: scattered light Power Supply: 24 VAC/VDC Relay outputs: potential-free Alarm relay locked: 1 changeover contact 250 V, 8 A 1 opening contact 250 V, 8 A Contamination relay: 1 opening contact 250 V, 6 A Operating temperature: -20 °C – +50 °C Rated relative humidity: 10 – 95 % rh non-condensing Vds approved Rated flow velocity: 1 – 20 m / s Protection type: IP 65 |  | KRM-X-2-0,16

## Modbus Sensor
| Basic Description | Brief Description | Pic | Model Code
1 | DPT with Modbus Output (-250 -2500Pa) | DIGITAL DIFFERENTIAL PRESSURE OR AIR FLOW TRANSMITTER-WITH MODBUS COMMUNICATION Make: HK Instruments Oy (Made in Finland) Model: DPT-MOD-2500-D Range: -250 Pa to 2500 Pa Power supply: 24 VAC or VDC Output: Via Modbus Interface: RS485 selectable via menu or via Modbus Multiple field selectable measurement units: o Volume flow: m3/s, m3/h, cfm, l/s o Velocity: m/s, ft./min o Pressure: Pa, inWC, mmWC, kPa, mbar, psi With Display Display: 2-line display (12 characters/line) Line 1: Direction of control output Line 2: Pressure or air flow measurement, selectable via menu |  | DPT-MOD-2500-D
2 | DPT with Modbus Output (-250 -7000Pa) | DIGITAL DIFFERENTIAL PRESSURE OR AIR FLOW TRANSMITTER- WITH MODBUS COMMUNICATION Make: HK Instruments Oy (Made in Finland) Model: DPT-MOD-7000-D Range: -250 Pa ... 7000 Pa Power supply: 24 VAC or VDC Output: Via Modbus Interface: RS485 Zero point calibration: Manual pushbutton & Via Modbus Response Time: 1.0 to 20 s, selectable via menu or via Modbus Multiple field selectable measurement units: o Volume flow: m3/s, m3/h, cfm, l/s o Velocity: m/s, ft./min o Pressure: Pa, inWC, mmWC, kPa, mbar, psi With Display Display: 2-line display (12 characters/line) Line 1: Direction of control output Line 2: Pressure or air flow measurement, selectable via menu |  | DPT-MOD-7000-D
3 | Dual DPT with Modbus | DIFFERENTIAL PRESSURE & AIR FLOW TRANSMITTER FOR AHU APPLICATION Model : DPT-Dual-MOD-AHU-D Make : HK Instruments Oy Range: -700...7000 Pa and -250...2500 Pa, Pressure: Pa, kPa, mbar, inchWC, mmWC, psi Flow: m3/s, m3/hr, cfm, l/s, m/s, ft/min Power supply: 24 VAC or VDC Output: Via Modbus Interface: RS485 Response Time: 1.0 to 20 s, selectable via menu or via Modbus register Input signals:2 x input (0...10 V, NTC10k, Pt1000, NI1000/(-LG), or (BIN IN) Zero point calibration options: Manual pushbutton & Via Modbus Multiple field selectable measurement units: o Volume flow: m3/s, m3/h, cfm, l/s o Velocity: m/s, ft./min o Pressure: Pa, inWC, mmWC, kPa, mbar, psi With Display 2-line display (12 characters/line) Line 1: active measurement, inlet A Line 2: active measurement, inlet B If inputs are selected, the lines show also input information (for example temperature) |  | DPT-Dual-MOD-AHU-D
4 | Air velocity transmitter with Display | AIR VELOCITY TRANSMITTER -WITH MODBUS COMMUNICATION Make : HK Instruments Oy Model : AVT-MOD-D Measuring units: ::Velocity ranges: 0...2/0...10/0...20m/s, ::Temperature range : 0...50 °C, Probe: OD 10 mm, length 210 mm from bottom of the cover Immersion Length with Flange: Adjustable 50–180mm Supply voltage: 24 VDC/VAC ± 10%, Output: Modbus RTU with Display |  | AVT-MOD-D
5 | Differential Pressure or Air flow transmitter With PID Controller ( With Modbus) | DIFFERENTIAL PRESSURE OR AIR FLOW TRANSMITTER WITH PID CONTROLLER (With Modbus Communication) Model : DPT-Ctrl-MOD-2500-D Make : HK Instruments Oy Range: -250...2500 Pa Power supply: 24 VAC or VDC Output : Via Modbus Interface : 485 PID - Parameter: Adjustable Via Menu Zero point calibration: Manual pushbutton & Via Modbus Response Time: 1.0 to 20 s, selectable via menu or via Modbus Multiple field selectable measurement units: o Volume flow: m3/s, m3/h, cfm, l/s o Velocity: m/s, ft./min o Pressure: Pa, inWC, mmWC, kPa, mbar, psi With Display Display: 2-line display (12 characters/line) Line 1: Direction of control output Line 2: Pressure or air flow measurement, selectable via menu |  | DPT-Ctrl-MOD-2500-D
6 | ROOM CO2 TRANMITTER / CONTROLLER WITH MODBUS | ROOM CO2 TRANMITTER / CONTROLLER WITH MODBUS Make : Produal Oy Model : RTX-Co2-rH-Mod Measurement Range: Temperature: 0....50°C Relative Humidity: 0- 100%rH Operating temperature Range: 0 ... +50 °C CO₂ measurement range : 0...5000 ppm Power supply: 24 VAC or VDC, ±10 %, Output: Modbus via RS485 Accuracy : 2% rH Temperature Accuracy : ±0.3 °C, Protection class: IP20 Without Display |  | RTX-Co2-rH-Mod
7 | Touchscreen Room Transmitter With Modbus | Touchscreen Room Transmitter Make : Produal Oy Model : RTX-D-RH-MOD Humidity measurement range : 0...100 %rH Humidity measurement accuracy : ±2 %rH Temperature measurement range : 0...50 °C Temperature measurement accuracy : ±0.3 °C IP protection class : IP30 Ambient temperature : 0...60 °C Ambient humidity : 0...95 %rH Product dimensions : 99 x 99 x 27 mm Materials : ABS plastic With Display |  | RTX-D-RH-MOD
8 | CO2- VOC - Humdity- Temperature - 0-10V, With Display -With Modbus | Touchscreen Room Transmitter Make : Produal Oy Model : RTX-CO2-D-RH-VOC-MOD VOC measurement range : 0...32767 ppm CO₂ measurement range : 0...5000 ppm CO₂ measurement accuracy : ±40 ppm +2 % Humidity measurement range : 0...100 %rH Humidity measurement accuracy : ±2 %rH Temperature measurement range : 0...50 °C Temperature measurement accuracy : ±0.3 °C Multifunctional input : 1 x NTC 10 / Pt1000 / Resistive / Digital / 0...10 Vdc and 1 x NTC 10 / Resistive / Digital IP protection class : IP30 Ambient temperature : 0...60 °C Ambient humidity : 0...95 %rH Product dimensions : 99 x 99 x 27 mm Materials : ABS plastic With Display |  | RTX-CO2-D-RH-VOC-MOD
9 | Configuration tool | Note : You need one Commising tool MYT-CON, attaching to the transmitter. Thus from tools you can set Modbus resister in the devices. Configuration tool, Model: MYT-CON Make : Produal Oy Compatible products : CU-LH IP, protection class : IP20, Ambient temperature : 0...50 °C Ambient humidity : 0...85 %rH Product dimensions : 79 x 25 x 13 mm Materials : ABS plastic |  | MYT-CON
10 | Duct Temp. & Humidity | HUMIDITY & TEMPERATURE TRANSMITTER -(With Modbus Communication) Model : KLK-M Make : Produal Oy Measurement Range : Temperature: -50 ... 50 DegC Relative Humidity : 0- 100%rH Accuracy: Temperature: ±0.5 degree C / Relative humidity: ±2 % Output: Modbus vis RS485 Probe Dimension:∅ 8 mm x 220 mm Protection class:IP54 Without display Acc: with Adjustable flange |  | KLK-M
11 | For Modbus Commissing need Transmitter Commising tool | TRANSMITTER COMMISING TOOL Model : ML-SER Make : Produal Oy Supply :from master device Cable : 0.75 m Adapter :6 pin Display : white back-light, 2 x 16 character, |  | ML-SER
12 | Duct Temperature Sensor(Modbus output) | TEMPERATURE TRANSMITTER- (With Modbus Output) Model :TEK-M Make: Produal Oy Duct mounted sensor sensor: Pt1000 EN 60751/B output 1: 0...10 V Output 2: Modbus via RS485 Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Mounting: Duct adjustable via flange stem :Ø 8 mm x 200 mm, materialAISI316 housing: plastics protection class: IP54 ambient temperature: 0...+60 °C Without display Housing : IP20 Ambient temperature : 0...+50°C |  | TEK-M
13 | Immersion temperature transmitter -(Modbus output ) | IMMERSION TEMPERATURE TRANSMITTE -(With Modbus output) Model : TEAT-M-150 Make : Produal Oy Supply Voltage: 24vdc ....(15...35 Vdc) sensor: Pt1000 EN 60751/B Output 1 : 0-10 V Output 2: Modbus via RS485 Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Ambient temperature: 0...+60 °C Measuring probe dimensions :Ø 6 mm x 150 mm material : AISI 316L (acid-proof steel) IP protection :IP54 Ambient temperature : 0...60 °C with Thermowell Without Display |  | TEAT-M-150
14 | Room Temperature Transmitter -(Modbus Output ) | ROOM TEMPERATURE TRANSMITTER -(Modbus) Model : TEHR M Make : Produal Oy measuring ranges selectable : 0...+50 °C 0...+100 °C -50...+50 °C -50...+150 °C supply : 15...35 Vdc Output 1 : 0-10 V Output 2: Modbus via RS485 accuracy : ±0.5 °C at 25 °C ambient temperature : 0...+50 °C housing ABS plastic: IP20 dimensions : (w x h x d) 86 x 85 x 32 mm |  | TEHR-M
15 | Outdoor/ Ambient Temperature Transmitter -(Modbus Output ) | OUTDOOR/ AMBIENT TEMPERATURE TRANSMITTER- (with Modbus Communication) Make : Produal Oy Model : TEU-M Sensor element : Pt1000 EN 60751/B Supply : 15...35 Vdc Output 1 : 0-10 V Output 2: Modbus via RS485 Range: -50...50, -50...150, 0...50, 0...100 °C (selectable via jumper) Housing protection class IP54 (cable gland downwards) cable gland M16 dimensions (w x h x d) 115 x 115 x 45 mm Ambient temperature -30...60 °C |  | TEU-M
16 | Cable Temperature Transmitter -(Modbus Ouput) | CABLE TEMPERATURE TRANSMITTER -(With Modbus) Model : TEKY4-M Make : Produal Oy Ranges 0...50 °C 0...100 °C -50...50 °C -50...150 °C Supply : 15...35 Vdc Sensor element: Pt1000 EN60751/B Accuracy ±0.5 °C Output 1 : 0-10 V Output 2: Modbus via RS485 temperature transmitter for cold spaces Measuring probe sleeve : 4 mm x 30 mm, stainless steel ambient temperature -30...+80 °C cable : 3.2 mm x 2.3 m cable gland : M16 ambient temperature : -30...60 °C protection class IP54 Without Display |  | TEKY4 -M

## ROOM CONTROLLER
| Basic Description | Brief Description | Pic | Model Code
1 | Building Controller | Building Controller Model: CU Make : Produal Oy Power Supply : 24 Vac/dc Multifunctional output : 2 x 0...10 Vdc, 2 mA / 24 Vac, 1 A (PWM) and 2 x 0...10 Vdc, 2 mA Communication : Modbus RTU Supply output : 2 x 24 Vac, total load < 6 A Multifunctional input : 3 x NTC 10 / Resistive / Potential free contact / 0...10 Vdc IP protection class : IP44 Ambient temperature : 0...50 °C Ambient humidity : 0...85 %rH Product dimensions : 116 x 128 x 47 mm Mounting : on the wall surface or on 35 mm DIN rail Materials : PC plastic |  | CU
2 | Building Controller | Building Controller Model: CU-LH-MOD Make : Produal Oy Power Supply : 24 Vac/dc Multifunctional output : 2 x 0...10 Vdc, 2 mA / 24 Vac, 1 A (PWM) and 2 x 0...10 Vdc, 2 mA Communication : Modbus RTU Supply output : 2 x 24 Vac, total load < 6 A Multifunctional input : 3 x NTC 10 / Resistive / Potential free contact / 0...10 Vdc IP protection class : IP44 Ambient temperature : 0...50 °C Ambient humidity : 0...85 %rH Product dimensions : 116 x 128 x 47 mm Mounting : on the wall surface or on 35 mm DIN rail Materials : PC plastic |  | CU-LH-MOD
3 | Room controller | Room controller Model: HLS44 Make : Produal Oy Power Supply : 24 Vac/dc Set point : 18...26 °C, ±16 °C (day mode), 8...50 °C (night mode) Temperature measurement range : 0...50 °C Temperature measurement accuracy : ±0.5 °C Triac output : 2 x 24 Vac, 1 A Voltage input : 1 x 0...10 Vdc Digital input : 1 x potential free input Resistive input : 1 x NTC 10 / DI Voltage output : 4 x 0...10 Vdc, 2 mA IP protection class : IP20 Ambient temperature : 0...50 °C Ambient humidity : 0...85 %rH Product dimensions : 87 x 86 x 32 mm Mounting : with screws on wall or on a junction box (hole distance 60 mm) Materials : ABS plastic |  | HLS 44

## Wireless Sensor
| Basic Description | Brief Description | Pic | Model Code
1 | Wireless Base Unit | WIRELESS BASE UNIT-PRODUAL PROXIMA -WBU Make : Produal Oy Model : WBU Supply : 24 Vac/dc (22...26 V) Network frequency : 2,4 GHz Network range : up to 100 m indoors / up to 200 m in open air Network size: up to 100 transmitters Inputs: 6 x universal input (NTC 10 / Pt1000 / Resistive / Potential free contact /0...10 Vdc) Outputs: 6 x 0...10 Vdc / 2...10 Vdc, Supply output: 2 x 24 Vac Communication: Modbus RTU / Modbus TCP Commissioning tool : Produal MyTool® App Operating conditions : ::Temperature: --5...50 °C ::Humidity : 0...90% rH Housing : ABS, IP22 Dimensions (w x h x d): 186 x 136 x 55 mm Antenna connector: SMA |  | WBU
2 | Wireless Temperature Transmitter | Wireless Temperature Transmitter Model : WTR Make: Produal Oy, Supply: 3,6 V lithium battery (3600 mAh), Network frequency :2.4 GHz, Temperature measurement : Range : 0...50 °C Accuracy : ±0.5 °C Commissioning tool : Produal MyTool® App, Operating conditions : Temperature: 0...50 °C Housing : PC plastic, IP30 Mounting : on the wall surface Dimensions (w x h x d) : 97 x 97 x 33 |  | WTR
3 | Wireless Transmitter - Temperature and Humidity | WIRELESS ROOM TRANSMITTER-PRODUAL PROXIMA-WTR Model : WTR-RH Supply: 3,6 V lithium battery (3600 mAh) Network frequency :2.4 GHz Temperature measurement ::Range : 0...50 °C ::Accuracy : ±0.5 °C Humidity measurement ::Range 0...100 %rH ::Accuracy (25 °C) typ. ±3 %rH Commissioning tool : Produal MyTool® App Operating conditions : ::Temperature: 0...50 °C ::Humidity : 0...85% rH Housing : PC plastic, IP30 Mounting : on the wall surface Dimensions (w x h x d) : 97 x 97 x 33 |  | WTR-RH
4 | Wireless Transmitter- Input Module | Wireless Transmitter- Input Module Model : WTR-IM Make: Produal Oy, Supply: 3,6 V lithium battery (3600 mAh), or 10...30 Vdc / 12...28 Vac Network frequency :2.4 GHz, Temperature measurement : Range : 0...50 °C Accuracy : ±0.2 °C, Humidity Measurement : Range 0...100 %rH, Accuracy (25 °C) typ. ±2 %rH, Commissioning tool : Produal MyTool® App, Housing : PC plastic, Protection class IP30 Mounting : on the wall surface Dimensions (w x h x d) : 97 x 97 x 33 |  | WTR-IM
5 | Wireless Transmitter - Temperature & Occupancy | WIRELESS ROOM TRANSMITTER-PRODUAL PROXIMA-WTR Model : WTR-PIR Supply: 3,6 V lithium battery (3600 mAh) Network frequency :2.4 GHz Temperature measurement ::Range : 0...50 °C ::Accuracy : ±0.5 °C (PIR) Occupancy detection: Detection area up to 13 meters Display (D): Monochrome LCD display (Optional ) Commissioning tool : Produal MyTool® App Operating conditions : ::Temperature: 0...50 °C ::Humidity : 0...85% rH Housing : PC plastic, IP20 Mounting : on the wall surface Dimensions (w x h x d) : 97 x 97 x 33 mm |  | WTR-PIR
6 | Wireless Transmitter - Temperature and Humidity & Occupancy | WIRELESS ROOM TRANSMITTER-PRODUAL PROXIMA-WTR Model : WTR-RH-PIR Supply: 3,6 V lithium battery (3600 mAh) Network frequency :2.4 GHz Temperature measurement ::Range : 0...50 °C ::Accuracy : ±0.5 °C Humidity measurement ::Range 0...100 % rH ::Accuracy (25 °C) typ. ±3 % rH (PIR) Occupancy detection: Detection area up to 13 meters Display (D): Monochrome LCD display ( Optional) Commissioning tool : Produal MyTool® App Operating conditions : ::Temperature: 0...50 °C ::Humidity : 0...85% rH Housing : PC plastic, IP20 Mounting : on the wall surface Dimensions (w x h x d) : 97 x 97 x 33 mm |  | WTR-RH-PIR
7 | Wireless Transmitter - Temperature and CO2 | WIRELESS ROOM TRANSMITTER-PRODUAL PROXIMA-WTR Model : WTR- CO2 Supply: 3,6 V lithium battery (3600 mAh) Network frequency :2.4 GHz Temperature measurement ::Range : 0...50 °C ::Accuracy : ±0.5 °C CO2measurement ::Range0...5000ppm ::Accuracy typ. ±30 ppm ±3 % of value Display (D): Monochrome LCD display (Optional ) Commissioning tool : Produal MyTool® App Operating conditions : ::Temperature: 0...50 °C ::Humidity : 0...85% rH Housing : PC plastic, IP20 Mounting : on the wall surface Dimensions (w x h x d) : 97 x 97 x 33 mm |  | WTR-CO2
8 | Wireless Transmitter - Temperature and Humidity , Co2 | WIRELESS ROOM TRANSMITTER-PRODUAL PROXIMA-WTR Model : WTR- RH-CO2 Supply: 3,6 V lithium battery (3600 mA h) Network frequency :2.4 GHz Temperature measurement ::Range : 0...50 °C ::Accuracy : ±0.5 °C Humidity measurement ::Range 0...100 %rH ::Accuracy (25 °C) typ. ±3 %rH CO2measurement ::Range0...5000ppm ::Accuracy typ. ±30 ppm ±3 % of value Display (D): Monochrome LCD display (Optional ) Commissioning tool : Produal MyTool® App Operating conditions : ::Temperature: 0...50 °C ::Humidity : 0...85% rH Housing : PC plastic, IP20 Mounting : on the wall surface Dimensions (w x h x d) : 97 x 97 x 33 mm |  | WTR-RH-CO2
9 | Wireless Transmitter - Temperature ,CO2 & Occupancy | WIRELESS ROOM TRANSMITTER- PRODUAL PROXIMA-WTR Model : WTR-PIR-CO2 Supply: 3,6 V lithium battery (3600 mAh) Network frequency :2.4 GHz Temperature measurement ::Range : 0...50 °C ::Accuracy : ±0.5 °C (PIR) Occupancy detection: Detection area up to 13 meters CO2measurement ::Range0...5000ppm Display (D): Monochrome LCD display (Optional ) Commissioning tool : Produal MyTool® App Operating conditions : ::Temperature: 0...50 °C ::Humidity : 0...85% rH Housing : PC plastic, IP20 Mounting : on the wall surface Dimensions (w x h x d) : 97 x 97 x 33 mm |  | WTR-PIR-CO2
10 | Wireless Transmitter - Temperature and Humidity , CO2 & Occupancy | WIRELESS ROOM TRANSMITTER-PRODUAL PROXIMA-WTR Model : WTR-RH-PIR-CO2 Supply: 3,6 V lithium battery (3600 mAh) Network frequency :2.4 GHz Temperature measurement ::Range : 0...50 °C ::Accuracy : ±0.5 °C Humidity measurement ::Range 0...100 %rH ::Accuracy (25 °C) typ. ±3 %rH CO2measurement ::Range0...5000ppm ::Accuracy typ. ±30 ppm ±3 % of value (PIR) Occupancy detection: Detection area up to 13 meters Display (D): Monochrome LCD display ( Optional) Commissioning tool : Produal My Tool® App Operating conditions : ::Temperature: 0...50 °C ::Humidity : 0...85% rH Housing : PC plastic, IP20 Mounting : on the wall surface Dimensions (w x h x d) : 97 x 97 x 33 mm |  | WTR-RH-PIR-CO2

## FLAMEPROOF TRANSMITTER
| Basic Description | Brief Description | Pic | Model Code
1 | DIFFERENTIAL PRESSURE TRANSMITTER, WITH FLAMEPROOF ENCLOSURE WITHOUT DISPLAY | DIFFERENTIAL PRESSURE TRANSMITTER, WITH FLAMEPROOF ENCLOSURE Make : HK Instruments Model : DPT2500-R8 With FLP Enclosure Measurement Range : ±100, 100, 250, 500,1000, 1500, 2000, 2500 Pa Accuracy : ±1% (from applied pressure) Supply voltage : 24 VAC or VDC, ±10 % Output signal : 0 ... 10 V or 4 ... 20 mA, 3-wire Zero point calibration: Automatic autozero or manual pushbutton Protection standard : IP 66 Housing materials : Cast Aluminum Alloy, LM-6 construction Flameproof enclosure : PESO & CIMFR certificate for FLP-JB-IIC enclosure Without Display |  | DPT2500-R8 With FLP Enclosure
2 | DIFFERENTIAL PRESSURE TRANSMITTER, WITH FLAMEPROOF ENCLOSURE WITH DISPLAY | DIFFERENTIAL PRESSURE TRANSMITTER, WITH FLAMEPROOF ENCLOSURE Make : HK Instruments Model : DPT2500-R8-D With FLP Enclosure Measurement Range : ±100, 100, 250, 500,1000, 1500, 2000, 2500 Pa Accuracy : ±1% (from applied pressure) Supply voltage : 24 VAC or VDC, ±10 % Output signal : 0 ... 10 V or 4 ... 20 mA, 3-wire Zero point calibration: Automatic autozero or manual pushbutton Protection standard : IP 66 Housing materials : Cast Aluminum Alloy, LM-6 construction Flameproof enclosure : PESO & CIMFR certificate for FLP-JB-IIC enclosure With Display |  | DPT2500-R8-D With FLP Enclosure
3 | AIR FLOW AND VELOCITY TRANSMITTER WITH FLAMEPROOF ENCLOSURE | AIR FLOW AND VELOCITY TRANSMITTER WITH FLAMEPROOF ENCLOSURE Make : HK Instruments Model : DPT-Flow-1000-D With FLP Enclosure Measurement Rang : 0−1000 Pa Accuracy : ±1% (from applied pressure) Supply voltage : 24 VAC or VDC, ±10 % Output signal : 0 ... 10 V or 4 ... 20 mA, 3-wire Zero point calibration: Automatic autozero or manual pushbutton Display : Backlit display, 2- line display (12 characters/line) Line 1: Air volume flow or velocity measurement Line 2: Pressure measurement Protection standard : IP 66 Housing materials : Cast Aluminum Alloy, LM-6 construction Flameproof enclosure : PESO & CIMFR certificate for FLP-JB-IIC enclosure |  | DPT-Flow-1000-D With FLP Enclosure
4 | ATEX DIFFERENTIAL PRESSURE SWITCH | ATEX DIFFERENTIAL PRESSURE SWITCH Ex zones 1, 2 and 21, 22 with ATEX type examination Make: Beck GmbH (Made in Germany) Model: 930.86.EX.122 231 Range: 500 - 2500 PA Switching differential: 150 Pa Temperature of media from –20°C to +85°C Diaphragm: Silicone, free of gas emissions Pressure connection: external diameter 6.0 mm PC Material: 2 plastic pipe connection pieces (P1 and P2) Deviation: ≤±15 %, min. ±10 Pa Drift: ≤±15 % Maximum operating pressure: 10 kPa Switch type: SPDT (1NO + 1NC) Contacts rating: max. 100 mA / 24 VAC, 30 mA / 24VDC Electrical connection: Tab terminal 6.3 mm x 0.8 mm Housing materials: Switch body and cover of plastic Protection: IP54 wiith Protection cap Cable entry: M20x1.5 with cable strain relief |  | 930.86.EX.122 231
5 | FLAMEPROOF DIFFERENTIAL PRESSURE TRANSMITTER | FLAMEPROOF DIFFERENTIAL PRESSURE TRANSMITTER Make: Beck GmbH (Made in Germany) Supply Voltage: 24 VDC Output: 4 ... 20 mA, 2‐wire Linearity: ≤ ±0.5% FS, min. ±1 Pa Response time: 0.2 s and 1 s (standard) Housing: Aluminium dia cast IP68 Working and storage temperature: -20 ... +70°C Hose connection with 6 mm outer diameter Electrical connection: Screw terminal block for wires and strands up to 1.5 mm2 1. Model: 982R.654206 (0-100 mmWC) with Flameproof enclosure 2. Model: 982R.664206 (0-250 mmWC) with Flameproof enclosure 3. Model: 982R.674206 (0-500 mmWC) with Flameproof enclosure 4. Model: 982R.6X4206 (± 250 mmWC) with Flameproof enclosure 5. Model: 982R.6X4206 (± 500 mmWC) with Flameproof enclosure 6. Model: 982R.684206 (0-1000 mmWC) with Flameproof enclosure (Other pressure range available as per customer specific requirement)
6 | DIGITAL DIFFERENTIAL PRESSURE TRANSMITTER | DIGITAL DIFFERENTIAL PRESSURE TRANSMITTER Make: Beck GmbH (Made in Germany) Supply Voltage: 24 VAC/VDC Output: 4 ... 20 mA or 0 ... 10 V, 3-wire Switching output: (NPN-NO) with a max. capacity of 30 VDC/100 mA Linearity: ≤ ±0.5% FS, min. ±1 Pa Response time: 0.2 s and 1 s (standard) Display: LED, red, 4 digits Working and storage temperature: -20 ... +70°C Hose connection with 4 / 6 mm outer diameter Electrical connection: Screw terminal block for wires and strands up to 1.5 mm2 Flameproof Enclosure with glass window (IP66) Model: JB-FLP-IIC MOC: Cast Aluminium Alloy, LM-6 construction with 80 mm window for visualization Process connection: 2 No. entries with 6 mm connector for tubing Cable entry: 1 nos. with double compression cable gland for electric wiring Model-1: 985M.354314b + Flameproof Enclsoure (Range: 0 ... 100 mmWC / 0 ... 250 mmWC) Model-2: 985M.364314b + Flameproof Enclsoure (Range: 0 ... 250 mmWC / 0 ... 500 mmWC) Model-3: 985M.374314b + Flameproof Enclsoure (Range: 0 ... 500 mmWC / 0 ... 1000 mmWC) Model-4: 985M.3x4314b + Flameproof Enclsoure (Range: -250 ... 0 ... +250 mmWC) Model-5: 985M.3x4314b + Flameproof Enclsoure (Range: -500 ... 0 ... +500 mmWC) (Other pressure range available as per customer specific requirement)
7 | Level switch DG tank Flameproof ( Considering 1 meter tank ) | CAPACITANCE LEVEL SWITCH Model : LMC-HAX-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm Make : Trumen Technologies HAX: Aluminum Flameproof IIa, IIb and IIc T1:Material Temperature max 80*DegC, RD1: Sensor Type Single Rigid Rod probe, S4: Sensing Rope Material SS 304, IT: Insulation Type full PTFE insulated, G0: Inactive length None, W4: Stilling well material SS 304 PB2:Process Connection Type 1-1/2" BSP, C4:Process Connection Material SS 304, EIUSI: 2 SPDT relay O/P for 2 single point L1000mm: Probe Length 1meter length |  | LMC-HAX-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm
8 | Level Transmitter DG tank ( Considering 1 meter tank ) | CAPACITANCE LEVEL TRANSMITTER Model : TLC-HAX-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm Make : Trumen Technologies HAX: Aluminum Flameproof IIa, IIb and IIc T1:Material Temperature max 80*DegC, RD1: Sensor Type Single Rigid Rod probe, S4: Sensing Rope Material SS 304, IT: Insulation Type full PTFE insulated, G0: Inactive length None, W4: Stilling well material SS 304 PB2:Process Connection Type 1-1/2" BSP, C4:Process Connection Material SS 304, EIL: 4-20mA Loop powered O/P L1000mm: Probe Length 1meter length |  | TLC-HAX-T1-RD1-S4-IT-G0-W4- PB2-C4-EIL-L1000mm

## Automation
| Basic Description | Brief Description | Pic | Model Code
1 | Open-frame PLC board | Open-frame PLC board Make : Pixsys Model : EPL200-1A POWER SUPPLY : 24V AC/DC POWER CONSUMPTION : 5Watt/VA max OPERATING CONDITIONS : Temperature 0-45°C, humidity 35..95 RH% SEALING : IP20 PROCESSOR : ARM Cortex H7 @ 480MHz SERIAL COMMUNICATION : 2x RS485 (1 x terminal blocks + 1 x RJ45 connector) Modbus RTU Master/Slave ETHERNET : 1x 10 / 100 Mbit/s Base-T on RJ45 connector (Modbus TCP master/slave) USB : 1x USB 2.0 for backup DIGITAL : INPUTS 8 PNP + 2 NPN DIGITAL OUTPUTS : 4 PNP RELAYS : 4 x 5A relays + 4 x 10A relays ENCODER INPUTS : 3x (Res. 32 bit, 100 KHz) Push Pull ANALOGUE INPUTS : 4x TC type K S R J T E N B, PT100, PT500, PT1000, Ni100, PTC1K, NTC10K (ß 3435K), potentiometer 1 K, 150 K (50000 pts) 0..60mV (16000 pts) 2x 0..10V (54000 pts), 0/4..20mA (40000 pts) ANALOGUE OUTPUT : 1 x 0..10V / 4..20 mA PLC LOGICS PROGRAMMING : Logic Lab, standard IEC61131-3 (ST, IL, FBD,SFC, LADDER), cycle time 4ms |  | EPL200-1A
2 | HMI PLC Codesys | HMI PLC Codesys Make : Pixsys Model : TC570 DISPLAY (ORIENTABLE) : 7” TFT Wide 1024 x 600 TOUCH-SCREEN : Capacitive single touch POWER SUPPLY : 24V DC - 11,5W RAM : (P2-P3) eMMC 16GB, RAM 2GB / (P4) eMMC 32GB, RAM 4GB SERIAL PORT : 2x RS485 or 1x RS485 + 1x CAN open USB : (P2) 2x USB 2.0 / (P3-P4) 1x USB 3.0, 1x USB 2.0 ETHERNET : 1x 1Gbit/s - 1x 10/100Mbit/s OPERATING SYSTEM : Linux Yocto, Docker/Podman UPS : Built-in UPS for persistent variables SOFTWARE TOOL : CODESYS 3.5 PROTOCOLS : EtherCAT master, PROFINET device, EtherNet/IP adapter, Modbus RTU master and TCP master/slave, CANopen master, OPC UA server/client, MQTT client (encryption supported) VISUALIZATION : CODESYS TargetVisu/WebVisu PIXSYS PORTAL (VPN) : Remote control and assistance service (optional) |  | TC570
3 | MCM260X Analogue/Digital I/O modules | MCM260X Analogue/Digital I/O modules Make : Pixsys Model : MCM260X-3AD POWER SUPPLY : 12..24V AC0 CONSUMPTION : 50Watt/VA max DIGITAL INPUTS : 8 PNP 12..24V DC ENCODER/COUNTER INPUTS : 3 Enc./cont.32bit max.80KHz DIGITAL OUTPUTS : 8 PNP, 700mA max 3A Tot. ANALOGUE INPUTS : Universal SAMPLING TIME : Programmable up to 2,1ms (frequency up to 470Hz) DIGITAL INPUTS : up to 16 PNP overlapped to digital outputs, 12..24V DC ENCODER/COUNTER INPUTS : 4x Enc./cont.32bit, max.80KHz DIGITAL OUTPUTS : up to 16 PNP overlapped to digital inputs, 700mA max 3A Tot. ANALOGUE OUTPUTS : 2x selectable 4..20mA (40000pts.± 0,2% F.S.) or 0..10V DC (40000pts. ± 0,2% F.S.) GALVANICAL ISOLATION : From supply to analogue inputs/outputs to serial bus |  | MCM260X-3AD
4 | Repeater and Isolator | Repeater and Isolator RS485 Make : Pixsys Model : NET485-A Power supply : 24 V DC ±15% - galvanic isolation 1kV Power consumption : 1 Watt/VA Serial communication : 2x RS485 (1200..115200 Baud) galvanically isolated 1 kV Termination resistors : Internal, 330 ohm, on input and output channel Dimensions :18 x 90 x 64 mm - 1 modules DIN43880 Material : Box: polycarbonate V0; Front panel: silicone V0 Weight : Approx. 100 g Sealing : Box and terminal blocks: IP20 Operating conditions : Temperature 0..45 °C, humidity 35..95 RH% Certifications : CE |  | NET485-A
5 | Protocol converter | Protocol converter Make : Pixsys Model : CNV510-PBUS-RTU-A Power supply : 12..24 V DC ±15% Power consumption : 3 Watt/VA Reading memory : 512 Bytes Writing memory : 512 Bytes Serial communication : 1x RS485 (1200..115200 Baud) galvanically isolated Ethernet : 1x 10 / 100 Mbit/s Dimensions : 71 x 90 x 64 mm - 4 modules DIN43880 Material : Noryl V0 Weight : Approx. 250 g Sealing Box and terminal blocks: IP20 Operating conditions Temperature 0..45 °C, humidity 35..95 RH% |  | CNV510-PBUS-RTU-A
6 | Protocol converter PROFINET | Protocol converter PROFINET Make : Pixsys Model : CNV520-21AD-PNET-RTU Power supply : 12..24 V DC / 24 V AC ±15% Power consumption : 2W Analog input : 1 x 4...20mA 2 wires current/loop (30000 points) ±0,2% F.S. - min. 100 milliseconds (1...30 mean filter) Digital inputs : 2 x PNP galvanically isolated 2.5 kV Digital outputs : 1 x PNP 24 VDC - 30 mA max Dimensions : 36 x 90 x 84 mm - 2 modules DIN43880 Serial communication : 1 x RS485 Modbus -RTU, up to 128 nodes Material : Noryl V0 Weight : Approx. 250g Sealing : Box and terminal blocks: IP20 Operating conditions : Temperature 0..45 °C, humidity 35..95 RH% Configuration : via MyPixsysLab Ethernet : 1 x Fast Ethernet 10/100 Mbit, RJ45 Profinet |  | CNV520-21AD-PNET-RTU
7 | TRANSFORMER | TRANSFORMER Model: 230/24-15 Make : Produal Oy, Supply : 230 Vac (207...253 V), 15 VA Output : 12 / 24 Vac Maximum output load : 15 VA IP protection class : IP20 Ambient temperature : 0...40 °C Product dimensions : 35 x 87 x 60 mm Mounting : 35 mm DIN rail |  | 230/24-15
8 | Portable Magnetic Work Table | Portable Magnetic Work Table Make : Produal Oy Dimensions L X H X W : 348 mm X37 mm X 353 mm Weight : Approx. 1.5 kg Load Capacity : Maximum load: 8 kg* Opening Angle : 90° Operating Temperature : –20 °C to +45 °C Material Specifications: Main Body Material, PC-ABS (Flame Retardant), Rockwell Hardness (R scale, 23 °C, ISO 2039): 118 Flexural Strength (23 °C, ISO 527): 60 MPa Type: Neodymium (NdFeB), rubber coated Magnet Grade: N42 Pull Force per Magnet: Approx. 105 N (~10 kg) Thread Material : Steel Q235 (M4), Surface Finish, Rubber coated Electrical Insulation: Fully insulated Dimensions: 151 × 151 × 13 mm |  | Portable Magnetic Work Table
9 | Module PID Controller | Module PID Controller Make shinko Model : QTC1-4PT-AAAAMMM-00 POWER SUPPLY COMMUNICATION OPTIONS : With Power Supply host Communication function Wiring method : Terminal Block Type ----------------------------------------------------------------------------------------Communication Expansion Module Model : QMC1- MT 4 Point Analog I/O Module : QAMI-4 Digital I/O Module : QDM1 |  | QTC1-4PT-AAAAMMM-00